# Annex No. 4

to Cabinet of Ministers

Regulation No. 149

adopted on 18 March 2014

Requirements for Technical Indicators of the Building

1. The building envelopes of the building must correspond to the following indicators:

1.1. for buildings with energy consumption up to 25 kWh/m2 per year:

1.1.1. windows with triple pane glass are applied if heat transmittance coefficient value Uw does not exceed 0,8 W/m2K; and

1.1.2. heat transmittance coefficient U value of other building envelopes of the building, including thermal bridges, does not exceed 0.30 W/m2K, for roofs and covers — 0.2 W/m2K;

1.2. central ventilation system must possess recuperation, efficiency coefficient at least 75%;

1.3. air permeability coefficient of building envelopes (expressed as air leak n50 (h-1), if difference of pressure is 50 Pa) for the entire building must correspond to:

1.3.1. for buildings with energy consumption that is less or equal to 15 kWh/m2 per year, air permeability coefficient n does not exceed 0.6 h–1 for residential buildings and public buildings; and

1.3.2. for buildings with energy consumption that is above 15 kWh/m2 per year and less or equal to 25 kWh/m2 per year, air permeability coefficient n does not exceed 1.0 h–1 for residential buildings and 1.2 h–1 for public buildings;

1.4. total primary energy consumption for all buildings after the project implementation (total amount of hot water for heating and electricity consumption) must not exceed 150 kWh/m2 per year.

2. Total heating space of the building is determined in square metres (m2) by summing up the area of all rooms in which it is planned to ensure microclimate of rooms. Areas of rooms are determined on floors of the building between internal surfaces of walls (including basement and mansard). Staircase or part of its area is included in the area of the floor from which the stairs are leading upwards.

3. Indoor temperature of the building reaches 18 °C.

4. The technical design of the building or graphical part thereof must include:

4.1. general plan with specified cardinal directions, significant shading objects, dimensions thereof and height;

4.2. designs of the floors of the building M 1:100 or 1:200 with dimensions, construction type ("pie"), window and outer door labels;

4.3. facade with dimensions and areas of planes of the building envelopes, windows and doors of the building;

4.4. cross-cut scheme with marked places of units, construction type ("pie") labels, height marks and dimensions;

4.5. most important unit solutions: socle insulation, balcony and loggia insulation, window construction unit, cornice and roof insulation unit, units for thermal bridge prevention to other constructions; and

4.6. specifications of construction types ("pies") with specified materials, thickness of layers thereof, adjusted thermal conductivity of the relevant material (λ) and total heat transmittance coefficient of the construction (U).

Acting Minister

for Environmental Protection

and Regional Development,

Minister for Justice	Baiba Broka